## Service levels and control para
Load management
Service levels and control parameters
| Updated | 2023-12-08 08:20
Orion adjusts its load limiting parameters in response to customer loading levels with the aim of achieving the agreed service levels for supply to residential water heaters. This schedule provides a history of the key load limiting parameters and the degree of control exercised in relation to these parameters. Orion's charges are linked to the peak loading levels that are limited by Orion's load management activities - the aim of this schedule is to highlight the balance between quality of supply and Orion's charges to retailers.
|  | Residential |  | Business
|  | Measured over any 8 hour period |  | Measured over any 5 hour period
| Date | Longest off | Highest average off | Longest off | Highest average off
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '555MW' Peak period on/off trigger: '570MW / 555MW' Control period on/off trigger: '575MW / 560MW' from 1 May 2012
Comment: 'Opening limits and triggers set as a base from which changes can be applied to the extent required to meet customer demand - adjustments aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2012-05-01 | 1:14 | 0:17 | 1:11 | 0:15
| 2012-05-02 | 0:41 | 0:31 | 0:39 | 0:30
| 2012-05-03 | 0:41 | 0:31 | 0:35 | 0:26
| 2012-05-16 | 1:10 | 0:54 | 1:10 | 0:55
| 2012-05-17 | 1:10 | 0:54 | 0:41 | 0:20
| 2012-05-21 | 0:54 | 0:37 | 0:53 | 0:37
| 2012-05-22 | 1:35 | 1:10 | 1:28 | 1:08
| 2012-05-23 | 1:00 | 0:43 | 0:59 | 0:47
| 2012-05-24 | 1:10 | 0:57 | 1:11 | 0:56
| 2012-05-29 | 1:05 | 0:55 | 1:05 | 0:58
| 2012-05-30 | 1:14 | 0:56 | 1:03 | 0:58
| 2012-05-31 | 0:41 | 0:16 | 0:14 | 0:03
| 2012-06-01 | 0:10 | 0:01 | 0:00 | 0:00
| 2012-06-05 | 0:52 | 0:23 | 0:48 | 0:23
| 2012-06-06 | 5:21 | 4:42 | 3:11 | 2:32
Limit: '565MW' Peak period on/off trigger: '580MW / 565MW' Control period on/off trigger: '585MW / 570MW' from 11am 6 June
Limit: '575MW' Peak period on/off trigger: '590MW / 575MW' Control period on/off trigger: '595MW / 580MW' from 12:30pm 6 June
Comment: 'Progressive limit and trigger increases to meet loading levels and mitigate the extent to which service levels are exceeded during snow storm event'
| 2012-06-07 | 4:45 | 3:43 | 2:42 | 2:35
| 2012-06-08 | 4:45 | 3:03 | 1:47 | 1:34
Comment: 'Localised load limiting within the Islington area resulted in a brecah of service levels. Local area limit adjusted to resolve issue'
| 2012-06-09 | 1:00 | 0:43 | 0:31 | 0:08
| 2012-06-11 | 1:24 | 1:15 | 1:22 | 1:15
| 2012-06-12 | 3:22 | 3:02 | 2:03 | 2:00
| 2012-06-13 | 3:22 | 3:02 | 1:36 | 1:22
| 2012-06-14 | 2:35 | 2:14 | 2:04 | 2:01
| 2012-06-15 | 2:35 | 2:14 | 2:03 | 1:57
| 2012-06-16 | 1:19 | 1:04 | 0:41 | 0:32
| 2012-06-17 | 1:24 | 1:09 | 1:24 | 1:10
| 2012-06-18 | 2:59 | 2:38 | 2:04 | 1:59
| 2012-06-19 | 2:48 | 2:31 | 2:03 | 2:01
| 2012-06-20 | 2:48 | 2:31 | 1:05 | 0:58
| 2012-06-21 | 1:07 | 0:55 | 0:59 | 0:41
| 2012-06-22 | 1:53 | 1:41 | 1:52 | 1:44
| 2012-06-25 | 2:03 | 1:39 | 1:58 | 1:39
| 2012-06-26 | 2:03 | 1:39 | 1:51 | 1:38
| 2012-06-27 | 2:48 | 2:22 | 2:03 | 1:59
| 2012-06-28 | 1:44 | 1:29 | 1:22 | 1:10
| 2012-06-29 | 1:36 | 1:22 | 1:35 | 1:23
| 2012-06-30 | 0:34 | 0:10 | 0:01 | 0:00
| 2012-07-01 | 0:26 | 0:09 | 0:20 | 0:08
| 2012-07-02 | 1:57 | 1:41 | 1:57 | 1:41
| 2012-07-03 | 1:49 | 1:41 | 1:30 | 1:19
| 2012-07-04 | 1:34 | 1:20 | 1:10 | 0:54
| 2012-07-05 | 1:03 | 0:52 | 0:38 | 0:22
| 2012-07-06 | 0:43 | 0:20 | 0:02 | 0:01
| 2012-07-09 | 1:03 | 0:51 | 1:00 | 0:51
| 2012-07-10 | 1:17 | 1:04 | 1:16 | 1:07
| 2012-07-11 | 1:46 | 1:31 | 1:44 | 1:31
| 2012-07-12 | 0:42 | 0:26 | 0:29 | 0:06
| 2012-07-13 | 0:30 | 0:07 | 0:00 | 0:00
| 2012-07-18 | 0:49 | 0:20 | 0:31 | 0:16
| 2012-07-19 | 0:44 | 0:34 | 0:42 | 0:32
| 2012-07-20 | 1:17 | 1:05 | 1:17 | 1:05
| 2012-07-23 | 0:46 | 0:34 | 0:42 | 0:34
| 2012-07-24 | 1:54 | 1:33 | 1:50 | 1:35
| 2012-07-25 | 1:27 | 1:12 | 1:11 | 0:54
| 2012-07-26 | 1:30 | 1:17 | 1:29 | 1:20
| 2012-07-27 | 2:02 | 1:50 | 2:01 | 1:52
| 2012-07-30 | 1:18 | 1:01 | 1:16 | 1:04
| 2012-07-31 | 1:18 | 1:01 | 0:59 | 0:42
| 2012-08-01 | 1:00 | 0:45 | 0:16 | 0:04
| 2012-08-07 | 1:00 | 0:48 | 1:00 | 0:50
| 2012-08-08 | 1:00 | 0:48 | 0:44 | 0:32
| 2012-08-09 | 0:48 | 0:32 | 0:19 | 0:03
| 2012-08-10 | 0:20 | 0:02 | 0:00 | 0:00
| 2012-08-13 | 1:40 | 1:28 | 1:39 | 1:25
| 2012-08-14 | 1:40 | 1:28 | 0:46 | 0:34
| 2012-08-15 | 0:46 | 0:34 | 0:18 | 0:03
| 2012-08-20 | 0:20 | 0:04 | 0:20 | 0:05
| 2012-08-21 | 0:20 | 0:04 | 0:00 | 0:00
| 2012-08-22 | 0:30 | 0:03 | 0:28 | 0:04
| 2012-08-23 | 0:37 | 0:16 | 0:34 | 0:12
| 2012-08-30 | 0:25 | 0:11 | 0:24 | 0:11
| 2012-09-03 | 0:10 | 0:01 | 0:10 | 0:01
| 2012-09-04 | 1:23 | 0:35 | 1:16 | 0:33
| 2012-09-05 | 0:31 | 0:01 | 0:00 | 0:00
| 2012-09-11 | 1:25 | 1:08 | 1:19 | 1:10
| 2012-09-12 | 3:19 | 2:36 | 2:03 | 2:00
| 2012-09-13 | 1:30 | 1:14 | 1:30 | 1:17
| 2012-09-14 | 0:47 | 0:22 | 0:47 | 0:15
| 2012-09-17 | 1:10 | 0:58 | 1:08 | 0:59
| 2012-09-18 | 1:10 | 0:58 | 0:41 | 0:23
| 2012-09-19 | 0:19 | 0:01 | 0:12 | 0:01
| 2012-09-20 | 0:44 | 0:07 | 0:43 | 0:07
| 2012-09-21 | 0:44 | 0:07 | 0:20 | 0:05
| 2012-10-08 | 0:58 | 0:34 | 0:51 | 0:34
| 2012-10-09 | 0:31 | 0:09 | 0:00 | 0:00
| 2012-11-02 | 0:58 | 0:03 | 0:53 | 0:05
Comment: 'Load management response testing being carried out beginning 26 November 2012'
| 2012-11-27 | 4:57 | 3:41 | 0:00 | 0:00
| 2012-11-28 | 0:33 | 0:12 | 0:00 | 0:00
Comment: 'Load management exceeded service level targets in response to high loading levels caused by unseasonal weather coinciding with a capacity limitation during Transpower’s scheduled maintenance program at its Islington grid exit point.'
| 2012-11-29 | 5:44 | 4:26 | 2:35 | 2:14
| 2012-11-30 | 5:39 | 4:19 | 1:59 | 0:52
| 2012-12-01 | 3:55 | 2:30 | 0:17 | 0:02
| 2012-12-02 | 3:11 | 1:53 | 0:00 | 0:00
| 2012-12-03 | 3:11 | 2:02 | 0:00 | 0:00
| 2012-12-04 | 3:11 | 2:02 | 0:00 | 0:00
| 2012-12-05 | 0:12 | 0:00 | 0:00 | 0:00
| 2012-12-06 | 0:12 | 0:00 | 0:00 | 0:00
| 2012-12-08 | 3:15 | 2:05 | 0:00 | 0:00
| 2012-12-09 | 3:26 | 2:06 | 0:00 | 0:00
| 2012-12-10 | 1:09 | 0:10 | 1:09 | 0:08
| 2012-12-11 | 0:31 | 0:26 | 0:30 | 0:26
| 2012-12-16 | 0:45 | 0:03 | 0:29 | 0:04
| 2012-12-17 | 4:25 | 1:34 | 2:02 | 1:23
| 2012-12-18 | 4:21 | 1:19 | 0:35 | 0:10
| 2012-12-19 | 0:47 | 0:21 | 0:27 | 0:20
| 2012-12-20 | 3:01 | 1:27 | 1:45 | 1:20
| 2012-12-21 | 3:06 | 0:20 | 1:00 | 0:07
| 2012-12-22 | 0:54 | 0:04 | 0:40 | 0:05
| 2012-12-23 | 0:54 | 0:04 | 0:05 | 0:01
| 2012-12-24 | 4:21 | 0:21 | 1:57 | 0:14
| 2012-12-25 | 3:13 | 0:15 | 0:08 | 0:02
| 2012-12-26 | 0:10 | 0:02 | 0:08 | 0:02
| 2012-12-29 | 1:23 | 0:06 | 1:17 | 0:09
| 2012-12-30 | 0:55 | 0:04 | 0:00 | 0:00
| 2013-01-08 | 1:19 | 0:07 | 1:14 | 0:09
| 2013-01-09 | 1:19 | 0:07 | 0:00 | 0:00
| 2013-01-10 | 1:28 | 0:14 | 1:27 | 0:20
| 2013-01-11 | 4:25 | 0:22 | 2:01 | 0:15
| 2013-01-12 | 4:22 | 0:22 | 1:59 | 0:15
| 2013-01-13 | 2:38 | 0:13 | 0:00 | 0:00
| 2013-01-13 | 2:42 | 0:13 | 1:59 | 0:15
| 2013-01-14 | 3:05 | 0:15 | 1:59 | 0:15
| 2013-01-15 | 1:47 | 0:08 | 0:00 | 0:00
| 2013-01-23 | 5:01 | 4:35 | 0:00 | 0:00
| 2013-01-24 | 2:41 | 2:31 | 0:15 | 0:08
| 2013-01-25 | 2:42 | 2:31 | 0:16 | 0:08
| 2013-01-26 | 1:39 | 0:07 | 1:38 | 0:11
| 2013-01-27 | 1:47 | 0:08 | 0:00 | 0:00
| 2013-01-27 | 2:19 | 0:11 | 1:57 | 0:14
| 2013-01-28 | 3:10 | 0:15 | 1:59 | 0:15
| 2013-01-29 | 2:39 | 2:25 | 0:00 | 0:00
| 2013-01-30 | 3:14 | 2:25 | 2:02 | 0:24
| 2013-01-31 | 4:25 | 4:08 | 2:07 | 2:02
| 2013-02-01 | 1:51 | 1:35 | 0:00 | 0:00
| 2013-03-01 | 4:27 | 4:14 | 0:31 | 0:25
| 2013-03-02 | 2:01 | 1:44 | 0:00 | 0:00
| 2013-03-05 | 0:00 | 0:00 | 0:43 | 0:16
| 2013-03-13 | 0:55 | 0:35 | 0:00 | 0:00
| 2013-03-14 | 0:55 | 0:35 | 0:00 | 0:00
| 2013-03-19 | 2:19 | 2:01 | 0:00 | 0:00
| 2013-03-20 | 2:19 | 2:01 | 0:00 | 0:00
| 2013-03-23 | 3:10 | 2:30 | 0:00 | 0:00
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '575MW' Peak period on/off trigger: '590MW / 575MW' Control period on/off trigger: '595MW / 580MW' from 1 April 2013
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2013-04-03 | 1:50 | 1:38 | 0:00 | 0:00
| 2013-04-04 | 0:12 | 0:02 | 0:00 | 0:00
| 2013-04-10 | 4:23 | 4:10 | 0:06 | 0:04
| 2013-04-11 | 3:13 | 3:04 | 0:08 | 0:05
| 2013-04-16 | 1:01 | 0:32 | 0:00 | 0:00
| 2013-04-17 | 1:01 | 0:32 | 0:00 | 0:00
| 2013-04-19 | 4:15 | 4:01 | 0:00 | 0:00
| 2013-04-20 | 2:37 | 2:17 | 0:00 | 0:00
| 2013-05-06 | 0:46 | 0:29 | 0:44 | 0:32
| 2013-05-07 | 0:46 | 0:29 | 0:21 | 0:01
| 2013-05-08 | 0:43 | 0:14 | 0:39 | 0:16
| 2013-05-27 | 1:03 | 0:40 | 1:02 | 0:37
| 2013-05-28 | 4:30 | 3:26 | 2:02 | 2:01
| 2013-05-29 | 4:30 | 3:26 | 1:32 | 1:16
| 2013-05-30 | 0:28 | 0:04 | 0:00 | 0:00
| 2013-05-30 | 1:45 | 1:27 | 1:44 | 1:26
| 2013-05-31 | 0:58 | 0:38 | 0:40 | 0:36
| 2013-06-02 | 2:00 | 1:35 | 1:56 | 1:34
| 2013-06-03 | 2:00 | 1:35 | 0:48 | 0:29
| 2013-06-04 | 1:20 | 1:05 | 1:19 | 1:07
| 2013-06-05 | 0:56 | 0:40 | 0:26 | 0:06
| 2013-06-05 | 1:20 | 1:05 | 0:51 | 0:41
| 2013-06-06 | 0:56 | 0:40 | 0:21 | 0:05
| 2013-06-07 | 0:38 | 0:18 | 0:36 | 0:20
| 2013-06-17 | 0:33 | 0:12 | 0:31 | 0:10
| 2013-06-18 | 0:33 | 0:12 | 0:00 | 0:00
| 2013-06-19 | 1:00 | 0:45 | 1:05 | 0:47
| 2013-06-20 | 4:42 | 4:17 | 2:03 | 1:59
Comment: 'Significant load management with most customers finishing the day slightly above our 4 hour service level target. A small number of customers were exposed to further load management of water heaters due to a localised constraint which we have now resolved'
Comment: 'Additional generation support provided to mitigate water heating off-hours and reduce contribution to chargeable grid transmission peaks'
| 2013-06-21 | 6:13 | 5:46 | 2:09 | 2:02
Comment: 'Extended shedding in respose to higher than forecast load during severe weather. In addition to limit adjustment noted, network limit temporarially increased up to 30MW and additional generation support provided to return hot water service.'
Limit: '585MW' Peak period on/off trigger: '595MW / 585MW' Control period on/off trigger: '600MW / 590MW' from noon 21 June 2013.
| 2013-06-22 | 1:44 | 1:22 | 1:32 | 1:22
| 2013-06-23 | 1:32 | 1:22 | 0:26 | 0:14
| 2013-06-24 | 2:15 | 1:53 | 2:01 | 1:55
| 2013-06-25 | 2:04 | 1:51 | 2:03 | 1:52
| 2013-06-26 | 1:57 | 1:46 | 1:55 | 1:47
| 2013-06-27 | 2:03 | 1:47 | 2:00 | 1:48
| 2013-06-28 | 1:38 | 1:17 | 1:12 | 1:04
| 2013-07-01 | 1:29 | 1:14 | 1:29 | 1:14
| 2013-07-02 | 0:36 | 0:07 | 0:00 | 0:00
| 2013-07-09 | 1:27 | 1:03 | 1:25 | 1:08
| 2013-07-10 | 1:48 | 1:37 | 1:48 | 1:40
| 2013-07-11 | 2:32 | 2:16 | 2:03 | 1:59
| 2013-07-12 | 1:41 | 1:25 | 1:38 | 1:24
| 2013-07-13 | 0:36 | 0:07 | 0:00 | 0:00
| 2013-07-14 | 0:06 | 0:01 | 0:05 | 0:01
| 2013-07-15 | 1:05 | 0:49 | 1:06 | 0:51
| 2013-07-16 | 1:38 | 1:26 | 1:39 | 1:25
| 2013-07-17 | 1:00 | 0:47 | 0:39 | 0:13
| 2013-07-31 | 0:39 | 0:19 | 0:37 | 0:23
| 2013-08-01 | 0:59 | 0:34 | 0:45 | 0:32
| 2013-08-02 | 0:26 | 0:07 | 0:00 | 0:00
| 2013-08-07 | 0:02 | 0:00 | 0:00 | 0:00
| 2013-08-12 | 0:20 | 0:02 | 0:20 | 0:04
| 2013-08-13 | 0:41 | 0:17 | 0:40 | 0:17
| 2013-08-14 | 0:41 | 0:17 | 0:02 | 0:00
| 2013-08-29 | 0:43 | 0:26 | 0:39 | 0:25
| 2013-09-02 | 1:07 | 0:57 | 1:08 | 0:59
| 2013-09-03 | 0:42 | 0:19 | 0:37 | 0:16
| 2013-09-04 | 4:02 | 3:29 | 2:03 | 2:00
| 2013-09-05 | 4:02 | 3:29 | 2:03 | 2:00
| 2013-09-06 | 1:14 | 0:55 | 1:01 | 0:55
| 2013-09-16 | 0:23 | 0:02 | 0:10 | 0:04
| 2013-09-18 | 0:40 | 0:18 | 0:35 | 0:17
| 2013-09-19 | 0:26 | 0:08 | 0:21 | 0:07
| 2013-09-25 | 0:24 | 0:11 | 0:20 | 0:14
| 2013-09-26 | 0:15 | 0:01 | 0:00 | 0:00
| 2013-10-08 | 0:16 | 0:01 | 0:15 | 0:04
| 2013-10-09 | 0:15 | 0:01 | 0:00 | 0:00
| 2013-10-10 | 0:07 | 0:01 | 0:00 | 0:00
| 2013-11-20 | 1:06 | 1:02 | 0:13 | 0:02
| 2013-11-21 | 1:30 | 1:07 | 0:00 | 0:00
| 2013-11-22 | 2:33 | 2:10 | 0:19 | 0:04
| 2013-11-25 | 0:21 | 0:05 | 0:21 | 0:07
| 2013-11-26 | 1:18 | 1:08 | 0:00 | 0:00
| 2013-12-06 | 2:26 | 2:09 | 0:00 | 0:00
| 2013-12-09 | 0:05 | 0:01 | 0:04 | 0:00
| 2013-12-15 | 0:05 | 0:01 | 0:05 | 0:01
| 2014-01-11 | 0:06 | 0:02 | 0:05 | 0:01
| 2014-01-19 | 0:14 | 0:10 | 0:13 | 0:11
| 2014-01-21 | 0:43 | 0:02 | 0:31 | 0:04
| 2014-01-22 | 0:43 | 0:02 | 0:00 | 0:00
| 2014-01-23 | 1:11 | 0:10 | 1:11 | 0:09
| 2014-01-29 | 0:06 | 0:01 | 0:05 | 0:02
| 2014-02-06 | 0:06 | 0:01 | 0:05 | 0:01
| 2014-03-04 | 0:37 | 0:04 | 0:09 | 0:02
| 2014-03-05 | 0:37 | 0:04 | 0:10 | 0:01
| 2014-03-06 | 0:10 | 0:01 | 0:00 | 0:00
| 2014-04-01 | 0:11 | 0:02 | 0:10 | 0:02
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '575MW' Peak period on/off trigger: '590MW / 575MW' Control period on/off trigger: '595MW / 580MW' from 1 April 2014
Comment: 'Opening limits and triggers set to last year's opening levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2014-04-10 | 0:04 | 0:00 | 0:04 | 0:00
| 2014-04-11 | 0:02 | 0:00 | 0:00 | 0:00
| 2014-04-13 | 0:23 | 0:03 | 0:22 | 0:04
| 2014-04-14 | 0:35 | 0:05 | 0:18 | 0:08
| 2014-04-15 | 0:35 | 0:05 | 0:00 | 0:00
| 2014-04-16 | 0:21 | 0:18 | 0:21 | 0:18
| 2014-04-28 | 0:29 | 0:05 | 0:21 | 0:07
| 2014-04-29 | 0:51 | 0:26 | 0:49 | 0:33
| 2014-04-30 | 0:50 | 0:26 | 0:07 | 0:01
| 2014-05-13 | 0:03 | 0:00 | 0:00 | 0:00
| 2014-05-14 | 0:03 | 0:00 | 0:00 | 0:00
| 2014-05-16 | 0:36 | 0:14 | 0:36 | 0:19
| 2014-05-26 | 2:08 | 1:51 | 2:00 | 1:53
| 2014-05-27 | 2:11 | 1:52 | 2:01 | 1:50
| 2014-05-28 | 1:06 | 0:46 | 1:04 | 0:47
| 2014-05-29 | 0:14 | 0:01 | 0:00 | 0:00
| 2014-06-03 | 0:58 | 0:47 | 0:54 | 0:46
| 2014-06-04 | 0:43 | 0:25 | 0:40 | 0:23
| 2014-06-09 | 0:43 | 0:27 | 0:40 | 0:29
| 2014-06-10 | 0:43 | 0:30 | 0:37 | 0:26
| 2014-06-11 | 0:59 | 0:43 | 0:54 | 0:39
| 2014-06-12 | 0:59 | 0:43 | 0:09 | 0:01
| 2014-06-16 | 0:56 | 0:38 | 0:55 | 0:41
| 2014-06-17 | 0:56 | 0:38 | 0:00 | 0:00
| 2014-06-20 | 0:25 | 0:12 | 0:24 | 0:13
| 2014-06-23 | 0:45 | 0:23 | 0:39 | 0:30
| 2014-06-24 | 0:45 | 0:23 | 0:20 | 0:04
| 2014-06-25 | 0:28 | 0:06 | 0:00 | 0:00
| 2014-07-02 | 0:49 | 0:34 | 0:49 | 0:38
| 2014-07-03 | 1:09 | 0:50 | 1:06 | 0:51
| 2014-07-04 | 1:05 | 0:56 | 1:05 | 0:56
| 2014-07-07 | 0:40 | 0:07 | 0:33 | 0:07
| 2014-07-08 | 0:59 | 0:38 | 0:58 | 0:38
| 2014-07-09 | 0:59 | 0:35 | 0:12 | 0:01
| 2014-07-10 | 0:13 | 0:01 | 0:00 | 0:00
| 2014-07-15 | 0:38 | 0:10 | 0:34 | 0:13
| 2014-07-16 | 0:49 | 0:27 | 0:47 | 0:27
| 2014-07-17 | 0:56 | 0:41 | 0:48 | 0:40
| 2014-07-18 | 2:32 | 2:16 | 2:05 | 1:55
| 2014-07-19 | 0:55 | 0:20 | 0:13 | 0:01
| 2014-07-21 | 2:29 | 2:08 | 2:00 | 1:58
| 2014-07-22 | 2:29 | 2:08 | 2:01 | 1:55
Limit: '575MW' Peak period on/off trigger: '590MW / 570MW' Control period on/off trigger: '595MW / 575MW' from 9:30am 22 July 2014
Comment: 'Pricing period off-triggers adjusted to help achieve target annual duration and assist with extended duration of load shedding during the current southerly storm cycle.'
| 2014-07-23 | 1:43 | 1:27 | 0:50 | 0:28
| 2014-07-24 | 1:31 | 1:13 | 1:29 | 1:17
| 2014-07-25 | 1:16 | 0:56 | 1:09 | 0:58
| 2014-07-28 | 1:06 | 0:45 | 0:58 | 0:44
| 2014-07-29 | 0:46 | 0:13 | 0:00 | 0:00
| 2014-07-30 | 0:28 | 0:02 | 0:25 | 0:08
| 2014-08-04 | 0:41 | 0:24 | 0:38 | 0:23
| 2014-08-05 | 0:45 | 0:19 | 0:37 | 0:20
| 2014-08-08 | 1:00 | 0:37 | 0:55 | 0:30
| 2014-08-09 | 0:05 | 0:01 | 0:05 | 0:01
| 2014-08-12 | 0:31 | 0:14 | 0:33 | 0:17
| 2014-08-13 | 1:40 | 1:17 | 1:39 | 1:20
| 2014-08-14 | 4:14 | 3:58 | 2:10 | 2:02
| 2014-08-15 | 2:32 | 1:53 | 1:31 | 1:27
| 2014-08-18 | 0:47 | 0:22 | 0:39 | 0:20
| 2014-08-19 | 0:46 | 0:18 | 0:46 | 0:19
| 2014-08-20 | 0:46 | 0:18 | 0:18 | 0:04
| 2014-08-21 | 0:59 | 0:32 | 0:58 | 0:31
| 2014-08-22 | 1:02 | 0:50 | 1:00 | 0:52
| 2014-08-27 | 0:54 | 0:39 | 0:54 | 0:41
| 2014-08-28 | 0:40 | 0:14 | 0:38 | 0:10
| 2014-08-29 | 0:29 | 0:08 | 0:28 | 0:10
| 2014-09-01 | 0:30 | 0:04 | 0:23 | 0:04
| 2014-09-02 | 0:54 | 0:43 | 0:53 | 0:44
| 2014-09-04 | 0:26 | 0:06 | 0:25 | 0:04
| 2014-09-08 | 0:49 | 0:23 | 0:39 | 0:25
| 2014-09-09 | 0:48 | 0:23 | 0:33 | 0:16
| 2014-09-10 | 1:23 | 1:12 | 1:20 | 1:13
| 2014-09-11 | 0:55 | 0:35 | 0:54 | 0:36
| 2014-09-22 | 0:40 | 0:22 | 0:32 | 0:23
| 2014-09-23 | 1:11 | 1:01 | 1:10 | 1:04
| 2014-09-29 | 0:37 | 0:08 | 0:30 | 0:05
| 2014-10-03 | 0:29 | 0:12 | 0:27 | 0:10
| 2014-10-07 | 0:39 | 0:14 | 0:37 | 0:16
| 2014-10-15 | 0:45 | 0:26 | 0:41 | 0:29
| 2014-10-16 | 1:25 | 0:07 | 1:13 | 0:09
| 2014-10-17 | 1:25 | 0:07 | 0:00 | 0:00
| 2014-10-20 | 3:10 | 0:16 | 1:59 | 0:15
| 2014-10-21 | 3:10 | 0:16 | 0:37 | 0:08
| 2014-10-28 | 0:49 | 0:25 | 0:40 | 0:23
| 2014-10-30 | 0:56 | 0:38 | 0:53 | 0:38
| 2014-10-31 | 0:31 | 0:04 | 0:31 | 0:05
| 2014-11-03 | 1:14 | 0:17 | 1:10 | 0:16
| 2014-11-04 | 3:00 | 2:40 | 2:01 | 1:59
| 2014-11-05 | 4:05 | 3:34 | 2:04 | 2:00
| 2014-11-06 | 1:45 | 1:36 | 1:46 | 1:36
| 2014-11-07 | 0:37 | 0:13 | 0:38 | 0:19
| 2014-11-12 | 0:21 | 0:04 | 0:21 | 0:04
| 2014-11-13 | 1:52 | 1:38 | 1:48 | 1:38
| 2014-11-16 | 4:21 | 0:22 | 1:57 | 0:14
| 2014-11-17 | 3:05 | 0:31 | 1:53 | 0:34
| 2014-11-18 | 1:00 | 0:30 | 1:00 | 0:31
| 2014-11-19 | 4:25 | 0:38 | 2:03 | 0:22
| 2014-11-20 | 2:41 | 0:49 | 1:59 | 0:47
| 2014-11-24 | 0:23 | 0:01 | 0:08 | 0:01
| 2014-11-25 | 1:00 | 0:41 | 0:59 | 0:43
| 2014-11-26 | 1:00 | 0:41 | 0:18 | 0:04
| 2014-11-28 | 0:44 | 0:02 | 0:18 | 0:01
| 2014-11-29 | 0:05 | 0:01 | 0:00 | 0:00
| 2014-12-01 | 0:24 | 0:08 | 0:20 | 0:07
| 2014-12-10 | 0:07 | 0:01 | 0:05 | 0:01
| 2014-12-24 | 0:40 | 0:04 | 0:38 | 0:04
| 2014-12-25 | 0:51 | 0:05 | 0:48 | 0:05
| 2014-12-28 | 2:19 | 0:20 | 1:58 | 0:28
| 2014-12-29 | 1:04 | 0:08 | 0:00 | 0:00
| 2015-01-04 | 4:21 | 0:22 | 1:59 | 0:15
| 2015-01-05 | 4:26 | 0:22 | 2:02 | 0:15
| 2015-01-06 | 4:26 | 0:22 | 0:56 | 0:07
| 2015-01-07 | 0:22 | 0:01 | 0:00 | 0:00
| 2015-01-08 | 0:42 | 0:02 | 0:40 | 0:05
| 2015-01-09 | 3:12 | 2:45 | 2:03 | 2:00
| 2015-01-10 | 1:55 | 1:28 | 1:34 | 1:05
| 2015-01-12 | 1:46 | 0:09 | 1:34 | 0:13
| 2015-01-13 | 1:46 | 0:09 | 0:35 | 0:04
| 2015-01-14 | 0:07 | 0:01 | 0:06 | 0:01
| 2015-01-15 | 0:35 | 0:27 | 0:33 | 0:28
| 2015-01-19 | 0:34 | 0:02 | 0:34 | 0:02
| 2015-01-20 | 0:34 | 0:02 | 0:00 | 0:00
| 2015-01-26 | 0:36 | 0:04 | 0:35 | 0:07
| 2015-01-27 | 0:36 | 0:04 | 0:14 | 0:01
| 2015-01-29 | 0:06 | 0:02 | 0:05 | 0:02
| 2015-02-02 | 1:01 | 0:05 | 0:59 | 0:07
| 2015-02-03 | 0:50 | 0:03 | 0:11 | 0:02
| 2015-02-07 | 0:02 | 0:00 | 0:01 | 0:00
| 2015-02-12 | 2:17 | 0:11 | 2:01 | 0:15
| 2015-02-13 | 1:45 | 0:08 | 0:00 | 0:00
| 2015-02-16 | 0:07 | 0:01 | 0:06 | 0:01
| 2015-02-17 | 0:30 | 0:05 | 0:29 | 0:07
| 2015-02-18 | 0:23 | 0:04 | 0:13 | 0:02
| 2015-02-26 | 3:38 | 0:19 | 2:02 | 0:15
| 2015-03-02 | 4:10 | 0:21 | 1:57 | 0:14
| 2015-03-03 | 4:10 | 0:21 | 0:09 | 0:01
| 2015-03-05 | 0:27 | 0:01 | 0:01 | 0:00
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '575MW' Peak period on/off trigger: '590MW / 570MW' Control period on/off trigger: '595MW / 575MW' from 1 April 2015
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2015-04-13 | 0:30 | 0:08 | 0:30 | 0:11
| 2015-04-14 | 1:49 | 1:29 | 1:47 | 1:34
| 2015-04-15 | 0:38 | 0:14 | 0:06 | 0:01
| 2015-05-16 | 0:19 | 0:06 | 0:18 | 0:10
| 2015-05-25 | 2:22 | 1:01 | 2:02 | 1:04
| 2015-05-26 | 1:48 | 1:32 | 1:41 | 1:29
| 2015-05-27 | 0:41 | 0:29 | 0:38 | 0:29
| 2015-05-28 | 1:10 | 0:55 | 1:08 | 0:58
| 2015-05-29 | 1:38 | 1:21 | 1:37 | 1:22
| 2015-06-04 | 0:21 | 0:08 | 0:20 | 0:10
| 2015-06-05 | 0:37 | 0:09 | 0:37 | 0:14
| 2015-06-08 | 0:21 | 0:05 | 0:18 | 0:05
| 2015-06-15 | 0:42 | 0:30 | 0:41 | 0:29
| 2015-06-16 | 0:41 | 0:30 | 0:40 | 0:31
| 2015-06-17 | 2:01 | 1:43 | 2:01 | 1:48
| 2015-06-18 | 2:04 | 1:47 | 1:58 | 1:49
| 2015-06-19 | 1:14 | 0:58 | 1:11 | 0:57
| 2015-06-22 | 4:32 | 4:05 | 2:46 | 2:38
Comment: 'Extended shedding in response to prolonged cold weather and afternoon load being higher than forecast. Generation support deployed to mitigate impact.'
| 2015-06-23 | 3:15 | 3:06 | 2:05 | 2:01
| 2015-06-24 | 2:56 | 2:41 | 2:05 | 2:01
| 2015-06-25 | 4:01 | 3:30 | 2:04 | 2:01
| 2015-06-26 | 2:22 | 2:08 | 2:04 | 2:01
| 2015-06-30 | 0:34 | 0:06 | 0:26 | 0:05
| 2015-07-01 | 0:21 | 0:07 | 0:20 | 0:07
| 2015-07-02 | 0:38 | 0:05 | 0:19 | 0:05
| 2015-07-06 | 0:13 | 0:01 | 0:13 | 0:01
| 2015-07-07 | 1:41 | 1:24 | 1:41 | 1:23
| 2015-07-08 | 3:59 | 3:13 | 2:06 | 2:00
| 2015-07-09 | 1:38 | 1:21 | 1:32 | 1:23
| 2015-07-10 | 1:38 | 1:17 | 1:34 | 1:18
| 2015-07-11 | 0:05 | 0:01 | 0:04 | 0:01
| 2015-07-13 | 2:22 | 1:59 | 2:03 | 1:57
| 2015-07-14 | 1:11 | 0:55 | 1:11 | 0:53
| 2015-07-20 | 2:40 | 1:43 | 2:03 | 1:28
| 2015-07-21 | 2:59 | 1:36 | 2:00 | 1:32
| 2015-07-22 | 1:50 | 1:11 | 1:49 | 1:17
| 2015-07-23 | 1:29 | 0:26 | 1:29 | 0:36
| 2015-07-24 | 1:16 | 0:07 | 1:13 | 0:14
| 2015-07-29 | 1:06 | 0:13 | 1:04 | 0:12
| 2015-07-30 | 1:19 | 0:38 | 1:17 | 0:34
| 2015-07-31 | 1:00 | 0:47 | 0:54 | 0:47
| 2015-08-05 | 1:30 | 0:35 | 1:22 | 0:28
| 2015-08-06 | 2:20 | 1:19 | 1:59 | 1:03
| 2015-08-09 | 1:49 | 0:23 | 1:38 | 0:26
| 2015-08-10 | 2:41 | 1:32 | 2:00 | 1:16
| 2015-08-11 | 2:33 | 1:38 | 1:59 | 1:43
| 2015-08-12 | 2:36 | 2:05 | 2:03 | 1:54
| 2015-08-13 | 1:44 | 0:57 | 1:41 | 0:56
| 2015-08-17 | 1:24 | 0:52 | 1:15 | 0:51
| 2015-08-18 | 0:44 | 0:02 | 0:29 | 0:02
| 2015-08-20 | 0:41 | 0:10 | 0:33 | 0:17
| 2015-08-21 | 1:25 | 0:45 | 1:13 | 0:46
| 2015-08-24 | 1:46 | 0:47 | 1:35 | 0:41
| 2015-08-25 | 1:43 | 0:26 | 1:37 | 0:34
| 2015-08-26 | 1:32 | 0:52 | 1:28 | 1:01
| 2015-08-27 | 1:08 | 0:23 | 1:00 | 0:13
| 2015-08-28 | 0:10 | 0:01 | 0:10 | 0:01
| 2015-08-31 | 1:44 | 0:52 | 1:44 | 0:56
| 2015-09-01 | 4:12 | 3:48 | 2:03 | 1:59
| 2015-09-02 | 1:08 | 0:09 | 0:54 | 0:12
| 2015-09-03 | 0:55 | 0:07 | 0:55 | 0:06
| 2015-09-04 | 0:25 | 0:01 | 0:08 | 0:01
| 2015-09-07 | 2:58 | 1:33 | 2:04 | 1:39
| 2015-09-08 | 3:16 | 2:31 | 2:02 | 2:00
| 2015-09-09 | 2:04 | 1:41 | 1:59 | 1:37
| 2015-09-10 | 1:52 | 1:19 | 1:42 | 1:22
| 2015-09-11 | 2:03 | 1:15 | 1:59 | 1:32
| 2015-09-14 | 1:00 | 0:08 | 0:57 | 0:04
| 2015-09-21 | 0:39 | 0:07 | 0:20 | 0:02
| 2015-09-22 | 1:50 | 0:55 | 1:37 | 0:59
| 2015-09-23 | 0:05 | 0:01 | 0:04 | 0:01
| 2015-10-14 | 1:16 | 0:20 | 1:11 | 0:20
| 2015-10-15 | 1:31 | 0:28 | 1:20 | 0:23
| 2015-10-16 | 1:37 | 0:24 | 1:25 | 0:38
| 2015-10-20 | 2:23 | 1:34 | 1:59 | 1:26
| 2015-10-21 | 0:58 | 0:10 | 0:58 | 0:10
| 2015-10-22 | 2:01 | 0:30 | 1:52 | 0:29
| 2015-10-23 | 3:57 | 1:53 | 2:03 | 1:32
| 2015-10-27 | 3:08 | 1:42 | 2:02 | 1:28
| 2015-10-28 | 3:22 | 2:17 | 2:03 | 1:59
| 2015-10-29 | 3:28 | 2:57 | 2:02 | 1:58
| 2015-10-30 | 1:58 | 0:32 | 1:47 | 0:29
| 2015-11-03 | 1:22 | 0:11 | 1:09 | 0:13
| 2015-11-04 | 4:19 | 3:44 | 2:02 | 1:59
| 2015-11-05 | 2:18 | 1:20 | 1:59 | 1:24
| 2015-11-06 | 1:09 | 0:10 | 0:56 | 0:11
| 2015-11-09 | 0:56 | 0:05 | 0:56 | 0:07
| 2015-11-10 | 1:42 | 0:18 | 0:39 | 0:07
| 2015-11-11 | 3:36 | 0:52 | 2:02 | 1:02
| 2015-11-12 | 2:40 | 1:55 | 2:00 | 1:30
| 2015-11-17 | 0:23 | 0:11 | 0:21 | 0:13
| 2015-11-18 | 0:34 | 0:21 | 0:34 | 0:25
| 2015-11-19 | 1:15 | 1:06 | 1:12 | 1:07
| 2015-11-20 | 1:23 | 1:12 | 1:20 | 1:13
| 2015-11-23 | 1:10 | 0:59 | 1:10 | 1:00
| 2015-11-24 | 1:33 | 1:20 | 1:30 | 1:20
| 2015-11-25 | 2:49 | 2:26 | 2:04 | 1:59
| 2015-11-26 | 1:43 | 1:29 | 1:17 | 0:59
| 2015-11-30 | 0:34 | 0:25 | 0:35 | 0:25
| 2015-12-01 | 3:45 | 1:41 | 1:50 | 1:32
| 2015-12-02 | 5:34 | 4:58 | 2:16 | 2:05
| 2015-12-03 | 1:25 | 1:10 | 1:20 | 1:07
| 2015-12-04 | 0:08 | 0:01 | 0:07 | 0:01
| 2015-12-08 | 0:25 | 0:06 | 0:16 | 0:03
| 2015-12-09 | 0:20 | 0:04 | 0:15 | 0:04
| 2015-12-10 | 2:04 | 1:51 | 2:00 | 1:52
| 2015-12-11 | 0:18 | 0:04 | 0:16 | 0:05
| 2015-12-14 | 1:14 | 0:53 | 1:10 | 0:53
| 2015-12-15 | 2:12 | 0:25 | 1:43 | 0:17
| 2015-12-16 | 2:30 | 2:16 | 2:03 | 1:59
| 2015-12-21 | 0:31 | 0:18 | 0:25 | 0:19
| 2016-02-29 | 0:05 | 0:01 | 0:04 | 0:01
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '575MW' Peak period on/off trigger: '590MW / 570MW' Control period on/off trigger: '595MW / 575MW' from 1 April 2016
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2016-05-09 | 0:34 | 0:20 | 0:34 | 0:22
| 2016-05-23 | 0:30 | 0:12 | 0:25 | 0:12
| 2016-05-24 | 0:12 | 0:01 | 0:12 | 0:02
| 2016-05-30 | 0:20 | 0:04 | 0:20 | 0:03
| 2016-05-31 | 1:07 | 0:50 | 1:03 | 0:49
| 2016-06-01 | 0:49 | 0:40 | 0:48 | 0:40
| 2016-06-02 | 1:04 | 0:52 | 1:03 | 0:55
| 2016-06-03 | 1:03 | 0:49 | 1:00 | 0:53
| 2016-06-07 | 0:58 | 0:49 | 0:57 | 0:50
| 2016-06-08 | 3:48 | 0:58 | 2:04 | 1:01
| 2016-06-09 | 1:47 | 0:10 | 1:46 | 0:12
| 2016-06-13 | 1:22 | 1:06 | 1:17 | 1:04
| 2016-06-14 | 0:26 | 0:20 | 0:23 | 0:19
| 2016-06-16 | 0:41 | 0:32 | 0:40 | 0:32
| 2016-06-17 | 1:08 | 0:54 | 1:05 | 0:53
| 2016-06-30 | 0:25 | 0:17 | 0:21 | 0:16
| 2016-07-01 | 1:05 | 0:55 | 1:03 | 0:56
| 2016-07-05 | 0:35 | 0:12 | 0:30 | 0:14
| 2016-07-06 | 1:44 | 1:25 | 1:39 | 1:25
| 2016-07-07 | 1:06 | 0:55 | 0:59 | 0:52
| 2016-07-09 | 1:27 | 0:09 | 1:27 | 0:07
| 2016-07-11 | 1:29 | 1:13 | 1:27 | 1:15
| 2016-07-12 | 2:18 | 2:03 | 2:04 | 1:59
| 2016-07-19 | 0:18 | 0:04 | 0:17 | 0:08
| 2016-07-20 | 0:29 | 0:18 | 0:24 | 0:19
| 2016-07-22 | 0:27 | 0:18 | 0:25 | 0:17
| 2016-07-25 | 1:27 | 1:58 | 2:04 | 1:59
| 2016-07-26 | 1:50 | 1:14 | 1:27 | 1:14
| 2016-07-27 | 0:37 | 0:31 | 0:37 | 0:31
| 2016-07-31 | 1:03 | 0:52 | 0:58 | 0:56
| 2016-08-01 | 2:33 | 2:11 | 2:07 | 2:01
| 2016-08-02 | 1:45 | 1:29 | 1:44 | 1:31
| 2016-08-03 | 0:48 | 0:33 | 0:45 | 0:31
| 2016-08-04 | 1:36 | 1:21 | 1:32 | 1:22
| 2016-08-05 | 3:09 | 2:40 | 2:04 | 2:00
| 2016-08-07 | 0:16 | 0:01 | 0:00 | 0:00
| 2016-08-08 | 4:29 | 4:14 | 2:05 | 2:01
Comment: 'Extended shedding in response to cold weather and afternoon load being higher than forecast. Generation support deployed to mitigate impact.'
| 2016-08-09 | 2:44 | 2:16 | 2:02 | 1:59
| 2016-08-10 | 3:21 | 3:02 | 2:05 | 1:53
| 2016-08-11 | 2:20 | 2:04 | 2:06 | 1:59
| 2016-08-12 | 7:50 | 2:37 | 2:06 | 2:01
| 2016-08-15 | 1:19 | 0:56 | 1:14 | 1:00
| 2016-08-16 | 1:24 | 1:04 | 1:14 | 1:05
| 2016-08-17 | 0:40 | 0:23 | 0:39 | 0:22
| 2016-08-18 | 1:33 | 1:17 | 1:33 | 1:16
| 2016-08-19 | 0:35 | 0:17 | 0:35 | 0:19
| 2016-08-23 | 0:35 | 0:21 | 0:35 | 0:20
| 2016-08-24 | 2:12 | 1:47 | 1:59 | 1:46
| 2016-08-25 | 0:22 | 0:07 | 0:19 | 0:07
| 2016-08-29 | 0:22 | 0:04 | 0:15 | 0:04
| 2016-09-07 | 0:36 | 0:16 | 0:35 | 0:16
| 2016-09-08 | 5:15 | 4:15 | 2:31 | 2:03
| 2016-09-09 | 2:00 | 1:50 | 1:58 | 1:50
| 2016-09-19 | 0:05 | 0:01 | 0:04 | 0:02
| 2016-09-21 | 0:25 | 0:02 | 0:17 | 0:02
| 2016-09-22 | 0:14 | 0:01 | 0:10 | 0:01
| 2016-09-29 | 0:29 | 0:01 | 0:28 | 0:02
| 2016-09-30 | 0:49 | 0:01 | 0:00 | 0:00
| 2016-10-10 | 0:20 | 0:11 | 0:19 | 0:13
| 2016-10-12 | 0:03 | 0:00 | 0:01 | 0:00
| 2016-10-13 | 0:22 | 0:01 | 0:13 | 0:02
| 2017-02-15 | 3:16 | 0:32 | 2:03 | 0:13
| 2017-02-16 | 6:13 | 2:47 | 2:03 | 1:58
| 2017-02-17 | 0:32 | 0:01 | 0:05 | 0:00
| 2017-03-02 | 1:52 | 1:29 | 1:42 | 1:32
| 2017-04-06 | 0:20 | 0:04 | 0:17 | 0:03
| 2017-04-12 | 0:12 | 0:10 | 0:12 | 0:10
| 2017-05-02 | 0:43 | 0:30 | 0:40 | 0:27
| 2017-05-04 | 0:42 | 0:14 | 0:25 | 0:08
| 2017-05-05 | 0:41 | 0:25 | 0:37 | 0:25
| 2017-05-09 | 0:21 | 0:11 | 0:24 | 0:14
| 2017-05-10 | 0:59 | 0:41 | 0:52 | 0:42
| 2017-05-14 | 4:51 | 1:23 | 2:08 | 0:41
| 2017-05-15 | 2:08 | 1:52 | 2:02 | 1:48
| 2017-05-16 | 2:19 | 0:51 | 0:54 | 0:49
| 2017-05-17 | 1:36 | 0:37 | 0:45 | 0:37
| 2017-05-19 | 1:48 | 1:27 | 1:48 | 1:27
| 2017-05-22 | 2:27 | 2:07 | 2:09 | 2:01
| 2017-05-23 | 1:42 | 1:29 | 1:38 | 1:28
| 2017-05-25 | 0:29 | 0:07 | 0:17 | 0:07
| 2017-05-26 | 1:04 | 0:46 | 0:56 | 0:41
| 2017-05-29 | 0:30 | 0:18 | 0:28 | 0:16
| 2017-05-30 | 0:09 | 0:01 | 0:09 | 0:01
| 2017-06-06 | 1:00 | 0:50 | 0:57 | 0:51
| 2017-06-07 | 1:03 | 0:49 | 1:00 | 0:50
| 2017-06-08 | 0:40 | 0:21 | 0:36 | 0:20
| 2017-06-09 | 1:17 | 1:01 | 1:16 | 0:59
| 2017-06-12 | 0:45 | 0:31 | 0:40 | 0:28
| 2017-06-13 | 0:43 | 0:25 | 0:44 | 0:27
| 2017-06-14 | 1:15 | 0:47 | 1:10 | 0:50
| 2017-06-15 | 2:28 | 2:05 | 2:04 | 2:01
| 2017-06-16 | 0:25 | 0:07 | 0:20 | 0:08
| 2017-06-19 | 0:25 | 0:07 | 0:20 | 0:09
| 2017-06-20 | 0:45 | 0:35 | 0:40 | 0:34
| 2017-06-21 | 1:06 | 0:45 | 1:04 | 0:48
| 2017-06-22 | 0:50 | 0:43 | 0:50 | 0:43
| 2017-06-23 | 0:39 | 0:25 | 0:36 | 0:24
| 2017-06-25 | 0:26 | 0:04 | 0:13 | 0:02
| 2017-06-26 | 3:14 | 2:42 | 2:04 | 2:00
| 2017-06-27 | 2:03 | 1:53 | 2:01 | 1:53
| 2017-06-28 | 1:08 | 0:55 | 1:06 | 0:59
| 2017-06-29 | 1:11 | 0:55 | 1:11 | 0:56
| 2017-06-30 | 0:47 | 0:34 | 0:44 | 0:31
| 2017-07-03 | 0:25 | 0:08 | 0:19 | 0:07
| 2017-07-04 | 1:26 | 1:05 | 1:26 | 1:04
| 2017-07-05 | 1:12 | 0:54 | 1:07 | 0:54
| 2017-07-06 | 3:41 | 1:11 | 1:59 | 1:11
| 2017-07-07 | 3:08 | 0:54 | 2:01 | 0:54
| 2017-07-10 | 0:29 | 0:07 | 0:24 | 0:08
| 2017-07-11 | 2:14 | 2:01 | 2:04 | 1:59
| 2017-07-12 | 5:39 | 4:50 | 2:35 | 2:32
| 2017-07-13 | 3:47 | 3:30 | 2:06 | 2:00
| 2017-07-14 | 1:15 | 0:55 | 1:13 | 0:53
| 2017-07-15 | 1:46 | 0:10 | 1:43 | 0:09
| 2017-07-16 | 2:40 | 0:18 | 2:00 | 0:13
| 2017-07-17 | 0:45 | 0:31 | 0:44 | 0:31
| 2017-07-18 | 0:08 | 0:00 | 0:00 | 0:00
| 2017-07-19 | 0:30 | 0:20 | 0:29 | 0:20
| 2017-07-24 | 0:55 | 0:41 | 0:55 | 0:46
| 2017-07-25 | 1:01 | 0:48 | 0:59 | 0:50
| 2017-07-26 | 1:20 | 1:04 | 1:17 | 1:04
| 2017-07-27 | 1:31 | 1:14 | 1:26 | 1:14
| 2017-07-28 | 1:39 | 1:24 | 1:29 | 1:23
| 2017-07-30 | 0:32 | 0:20 | 0:30 | 0:19
| 2017-07-31 | 2:23 | 2:10 | 2:05 | 2:00
| 2017-08-01 | 0:45 | 0:31 | 0:45 | 0:31
| 2017-08-02 | 0:49 | 0:38 | 0:44 | 0:38
| 2017-08-03 | 1:26 | 1:07 | 1:17 | 1:06
| 2017-08-04 | 3:01 | 2:27 | 2:06 | 1:59
| 2017-08-08 | 0:24 | 0:15 | 0:20 | 0:14
| 2017-08-09 | 0:36 | 0:16 | 0:30 | 0:15
| 2017-08-11 | 0:25 | 0:10 | 0:25 | 0:12
| 2017-08-14 | 3:05 | 2:37 | 2:05 | 1:59
| 2017-08-15 | 1:25 | 1:08 | 1:20 | 1:08
| 2017-08-16 | 1:12 | 0:57 | 1:10 | 0:59
| 2017-08-21 | 0:49 | 0:40 | 0:45 | 0:40
| 2017-08-22 | 1:58 | 1:40 | 1:53 | 1:39
| 2017-08-23 | 1:25 | 1:08 | 1:24 | 1:11
| 2017-08-24 | 0:51 | 0:41 | 0:53 | 0:42
| 2017-08-25 | 0:34 | 0:16 | 0:30 | 0:13
| 2017-08-31 | 0:17 | 0:01 | 0:17 | 0:01
| 2017-09-01 | 0:30 | 0:09 | 0:20 | 0:09
| 2017-09-04 | 0:24 | 0:13 | 0:23 | 0:14
| 2017-09-05 | 0:22 | 0:01 | 0:06 | 0:01
| 2017-09-08 | 0:23 | 0:10 | 0:20 | 0:12
| 2017-09-11 | 0:56 | 0:46 | 0:55 | 0:46
| 2017-09-12 | 0:45 | 0:36 | 0:41 | 0:35
| 2017-09-13 | 0:44 | 0:27 | 0:43 | 0:28
| 2017-09-14 | 0:45 | 0:38 | 0:45 | 0:38
| 2017-09-18 | 0:59 | 0:47 | 0:58 | 0:49
| 2017-11-02 | 0:50 | 0:30 | 0:19 | 0:03
| 2017-11-13 | 0:45 | 0:32 | 0:44 | 0:32
| 2017-11-14 | 0:56 | 0:40 | 0:52 | 0:40
| 2017-11-15 | 0:39 | 0:31 | 0:35 | 0:30
| 2017-11-16 | 0:23 | 0:05 | 0:15 | 0:05
| 2017-11-21 | 0:38 | 0:23 | 0:29 | 0:22
| 2017-11-22 | 0:46 | 0:32 | 0:45 | 0:36
| 2017-11-23 | 0:17 | 0:04 | 0:17 | 0:07
| 2017-11-24 | 0:35 | 0:23 | 0:33 | 0:26
| 2017-11-27 | 0:16 | 0:04 | 0:15 | 0:05
| 2017-11-28 | 0:55 | 0:43 | 0:50 | 0:42
| 2017-11-29 | 0:55 | 0:44 | 0:50 | 0:43
| 2017-11-30 | 0:49 | 0:37 | 0:46 | 0:38
| 2017-12-01 | 0:24 | 0:13 | 0:25 | 0:13
| 2017-12-04 | 5:11 | 4:36 | 2:07 | 2:00
| 2017-12-05 | 4:45 | 4:14 | 2:14 | 1:58
| 2017-12-06 | 0:56 | 0:46 | 0:55 | 0:49
| 2017-12-07 | 1:50 | 1:35 | 1:49 | 1:31
| 2017-12-08 | 4:58 | 4:28 | 2:05 | 1:59
| 2017-12-09 | 1:30 | 0:07 | 1:14 | 0:14
| 2017-12-11 | 4:46 | 4:10 | 2:01 | 1:59
| 2017-12-12 | 0:54 | 0:38 | 0:45 | 0:38
| 2017-12-13 | 1:13 | 0:56 | 1:10 | 0:55
| 2017-12-29 | 0:05 | 0:01 | 0:05 | 0:01
| 2018-01-22 | 3:12 | 0:25 | 2:03 | 0:14
| 2018-01-24 | 1:26 | 1:09 | 1:23 | 1:07
| 2018-01-30 | 0:17 | 0:02 | 0:17 | 0:04
| 2018-04-10 | 1:09 | 0:57 | 1:06 | 1:01
| 2018-04-11 | 2:37 | 2:22 | 2:05 | 2:00
| 2018-04-12 | 2:08 | 1:58 | 2:04 | 1:58
| 2018-05-23 | 0:25 | 0:13 | 0:20 | 0:14
| 2018-05-24 | 1:11 | 0:57 | 1:06 | 0:56
| 2018-05-25 | 1:03 | 0:46 | 1:03 | 0:50
| 2018-05-28 | 2:39 | 2:25 | 2:04 | 1:59
| 2018-05-29 | 2:08 | 1:46 | 2:00 | 1:44
| 2018-05-30 | 2:01 | 1:47 | 2:00 | 1:45
| 2018-05-31 | 1:48 | 1:32 | 1:46 | 1:32
| 2018-06-01 | 0:28 | 0:19 | 0:25 | 0:19
| 2018-06-06 | 3:51 | 3:04 | 2:05 | 1:59
| 2018-06-07 | 1:47 | 1:32 | 1:45 | 1:34
| 2018-06-08 | 0:24 | 0:06 | 0:19 | 0:07
| 2018-06-11 | 0:40 | 0:26 | 0:39 | 0:26
| 2018-06-12 | 0:44 | 0:31 | 0:41 | 0:32
| 2018-06-13 | 0:51 | 0:37 | 0:46 | 0:37
| 2018-06-18 | 1:42 | 1:23 | 1:41 | 1:22
| 2018-06-19 | 1:06 | 0:49 | 1:05 | 0:52
| 2018-06-20 | 1:07 | 0:57 | 1:04 | 0:58
| 2018-06-21 | 1:41 | 1:28 | 1:39 | 1:28
| 2018-06-22 | 3:59 | 3:35 | 2:04 | 2:01
| 2018-06-23 | 0:38 | 0:19 | 0:35 | 0:17
| 2018-06-25 | 1:59 | 1:43 | 1:53 | 1:41
| 2018-06-26 | 2:12 | 1:56 | 2:06 | 1:56
| 2018-06-27 | 1:45 | 1:23 | 1:44 | 1:25
| 2018-06-28 | 1:20 | 1:04 | 1:21 | 1:07
| 2018-06-29 | 1:29 | 1:06 | 1:28 | 1:07
| 2018-07-02 | 1:06 | 0:52 | 1:04 | 0:50
| 2018-07-03 | 1:48 | 1:34 | 1:47 | 1:36
| 2018-07-04 | 2:33 | 2:12 | 2:04 | 2:00
| 2018-07-05 | 2:30 | 2:11 | 2:04 | 2:00
| 2018-07-06 | 1:03 | 0:49 | 0:59 | 0:50
| 2018-07-10 | 0:19 | 0:08 | 0:19 | 0:05
| 2018-07-11 | 1:09 | 0:52 | 1:07 | 0:55
| 2018-07-13 | 0:47 | 0:26 | 0:36 | 0:27
| 2018-07-18 | 0:27 | 0:13 | 0:24 | 0:10
| 2018-07-19 | 1:03 | 0:47 | 0:57 | 0:47
| 2018-07-20 | 0:58 | 0:42 | 0:56 | 0:43
| 2018-07-23 | 1:14 | 1:04 | 1:14 | 1:04
| 2018-07-24 | 1:30 | 1:12 | 1:24 | 1:13
| 2018-07-25 | 3:20 | 2:01 | 3:28 | 2:01
| 2018-07-26 | 1:20 | 1:03 | 1:18 | 1:05
| 2018-07-27 | 1:24 | 1:09 | 1:22 | 1:10
| 2018-07-30 | 1:20 | 1:08 | 1:18 | 1:10
| 2018-07-31 | 0:22 | 0:05 | 0:15 | 0:02
| 2018-08-01 | 0:02 | 0:00 | 0:02 | 0:00
| 2018-08-02 | 1:22 | 0:51 | 1:22 | 0:53
| 2018-08-03 | 0:34 | 0:20 | 0:33 | 0:20
| 2018-08-06 | 0:20 | 0:05 | 0:15 | 0:04
| 2018-08-07 | 0:21 | 0:07 | 0:19 | 0:07
| 2018-08-08 | 0:07 | 0:01 | 0:00 | 0:00
| 2018-08-09 | 0:34 | 0:20 | 0:31 | 0:20
| 2018-08-13 | 0:21 | 0:08 | 0:15 | 0:07
| 2018-08-14 | 0:40 | 0:22 | 0:39 | 0:21
| 2018-08-15 | 0:25 | 0:12 | 0:20 | 0:13
| 2018-08-16 | 0:30 | 0:21 | 0:28 | 0:21
| 2018-08-20 | 2:26 | 2:11 | 2:04 | 2:01
| 2018-08-21 | 1:21 | 1:10 | 1:22 | 1:12
| 2018-08-22 | 1:40 | 1:16 | 1:42 | 1:19
| 2018-08-23 | 0:35 | 0:23 | 0:30 | 0:22
| 2018-08-24 | 0:40 | 0:19 | 0:39 | 0:23
| 2018-08-27 | 0:35 | 0:20 | 0:35 | 0:16
| 2018-08-28 | 0:32 | 0:15 | 0:30 | 0:17
| 2018-08-29 | 0:23 | 0:02 | 0:00 | 0:00
| 2018-08-30 | 1:03 | 0:49 | 1:01 | 0:48
| 2018-08-31 | 0:30 | 0:17 | 0:29 | 0:17
| 2018-09-03 | 2:54 | 2:31 | 2:05 | 2:00
| 2018-09-04 | 1:26 | 1:07 | 1:25 | 1:10
| 2018-09-05 | 1:12 | 0:54 | 1:04 | 0:53
| 2018-09-06 | 1:38 | 1:20 | 1:38 | 1:23
| 2018-09-07 | 2:24 | 2:08 | 2:05 | 1:59
| 2018-09-10 | 2:01 | 1:40 | 1:53 | 1:39
| 2018-09-11 | 1:05 | 0:55 | 1:03 | 0:55
| 2018-09-12 | 0:40 | 0:26 | 0:39 | 0:26
| 2018-09-13 | 0:30 | 0:19 | 0:30 | 0:20
| 2018-09-25 | 0:56 | 0:41 | 0:55 | 0:41
| 2018-09-26 | 0:25 | 0:10 | 0:20 | 0:08
| 2018-10-01 | 0:04 | 0:02 | 0:04 | 0:02
| 2018-10-02 | 0:30 | 0:12 | 0:30 | 0:13
| 2018-10-03 | 0:31 | 0:06 | 0:20 | 0:07
| 2018-10-04 | 0:44 | 0:27 | 0:44 | 0:26
| 2018-10-12 | 0:20 | 0:05 | 0:19 | 0:05
| 2018-10-15 | 0:25 | 0:10 | 0:19 | 0:09
| 2018-12-07 | 0:05 | 0:01 | 0:03 | 0:01
| 2018-12-08 | 0:04 | 0:00 | 0:02 | 0:00
| 2018-12-11 | 0:07 | 0:01 | 0:05 | 0:00
| 2018-12-15 | 0:08 | 0:01 | 0:08 | 0:01
| 2019-01-22 | 0:25 | 0:07 | 0:14 | 0:07
| 2019-01-23 | 5:06 | 4:40 | 2:10 | 2:01
Comment: 'Extended shedding in response to hot weather and high summer loads in the upper South Island region, anticipated southerly change was delayed. Water heating load progressively restored when service level limt reached."
| 2019-01-28 | 3:18 | 2:47 | 2:04 | 2:00
| 2019-01-29 | 0:07 | 0:00 | 0:00 | 0:00
| 2019-01-30 | 4:24 | 3:44 | 2:05 | 2:01
| 2019-01-31 | 0:26 | 0:08 | 0:20 | 0:08
| 2019-02-04 | 0:24 | 0:04 | 0:18 | 0:04
| 2019-02-05 | 0:38 | 0:22 | 0:34 | 0:20
| 2019-02-07 | 0:26 | 0:02 | 0:22 | 0:01
| 2019-02-08 | 0:06 | 0:00 | 0:05 | 0:00
| 2019-02-12 | 5:33 | 4:23 | 2:26 | 2:01
| 2019-02-13 | 0:27 | 0:07 | 0:19 | 0:04
| 2019-02-14 | 3:30 | 2:53 | 2:05 | 2:01
| 2019-02-15 | 0:16 | 0:02 | 0:11 | 0:01
| 2019-02-18 | 0:22 | 0:11 | 0:17 | 0:12
| 2019-02-19 | 1:02 | 0:28 | 0:53 | 0:25
| 2019-02-20 | 0:06 | 0:01 | 0:05 | 0:01
| 2019-02-21 | 0:49 | 0:36 | 0:48 | 0:39
| 2019-03-05 | 0:25 | 0:11 | 0:25 | 0:10
| 2019-03-06 | 0:30 | 0:19 | 0:30 | 0:19
| 2019-03-07 | 0:27 | 0:19 | 0:25 | 0:19
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '575MW' Peak period on/off trigger: '590MW / 570MW' Control period on/off trigger: '595MW / 575MW' from 1 April 2019
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2019-04-29 | 0:20 | 0:09 | 0:20 | 0:10
| 2019-04-30 | 0:24 | 0:11 | 0:24 | 0:10
| 2019-05-01 | 0:47 | 0:38 | 0:45 | 0:38
| 2019-05-14 | 0:18 | 0:02 | 0:18 | 0:03
| 2019-05-16 | 0:47 | 0:38 | 0:45 | 0:37
| 2019-05-17 | 1:22 | 1:07 | 1:20 | 1:08
| 2019-05-20 | 1:10 | 1:01 | 1:07 | 1:01
| 2019-05-21 | 0:30 | 0:17 | 0:29 | 0:13
| 2019-05-22 | 0:31 | 0:19 | 0:29 | 0:19
| 2019-05-23 | 0:25 | 0:07 | 0:22 | 0:09
| 2019-05-24 | 0:21 | 0:04 | 0:19 | 0:02
| 2019-06-03 | 0:19 | 0:02 | 0:17 | 0:02
| 2019-06-04 | 3:07 | 2:44 | 2:04 | 1:59
Comment: 'Extended shedding in response to cold weather, temporary 10MW limit increase applied to mitigate impact'
| 2019-06-05 | 5:09 | 4:31 | 2:06 | 2:01
Comment: 'Shedding continued to exceed service levels with higher limit and improving weather - permanent adjustment applied'
Limit: '590MW' Peak period on/off trigger: '605MW / 585MW' Control period on/off trigger: '610MW / 590MW' from 6 June 2019
| 2019-06-06 | 4:10 | 3:36 | 2:04 | 2:00
| 2019-06-07 | 2:16 | 1:52 | 1:59 | 1:51
| 2019-06-11 | 0:36 | 0:25 | 0:30 | 0:20
| 2019-06-12 | 0:15 | 0:01 | 0:15 | 0:02
| 2019-06-17 | 2:07 | 1:51 | 2:03 | 1:53
| 2019-06-18 | 2:34 | 2:15 | 2:06 | 1:59
| 2019-06-19 | 3:21 | 2:59 | 2:12 | 2:04
| 2019-06-20 | 3:11 | 2:47 | 2:07 | 2:01
| 2019-06-21 | 0:51 | 0:35 | 0:50 | 0:40
| 2019-06-23 | 0:36 | 0:20 | 0:36 | 0:19
| 2019-06-24 | 1:47 | 1:37 | 1:43 | 1:37
| 2019-06-25 | 2:03 | 1:50 | 1:56 | 1:50
| 2019-06-26 | 3:03 | 2:37 | 2:05 | 2:00
| 2019-06-27 | 3:40 | 3:16 | 2:04 | 2:01
| 2019-06-28 | 3:31 | 3:11 | 2:07 | 1:59
| 2019-06-29 | 0:24 | 0:11 | 0:20 | 0:11
| 2019-07-01 | 2:29 | 2:16 | 2:07 | 2:01
| 2019-07-02 | 1:48 | 1:31 | 1:45 | 1:29
| 2019-07-04 | 0:43 | 0:32 | 0:38 | 0:33
| 2019-07-05 | 2:43 | 2:21 | 2:03 | 1:59
| 2019-07-08 | 1:27 | 1:09 | 1:20 | 1:10
| 2019-07-09 | 1:50 | 1:35 | 1:48 | 1:33
| 2019-07-10 | 0:20 | 0:01 | 0:00 | 0:00
| 2019-07-15 | 0:22 | 0:14 | 0:20 | 0:17
| 2019-07-17 | 1:50 | 1:35 | 1:43 | 1:30
| 2019-07-18 | 1:34 | 1:22 | 1:34 | 1:22
| 2019-07-22 | 0:34 | 0:22 | 0:31 | 0:22
| 2019-07-23 | 0:20 | 0:07 | 0:14 | 0:02
| 2019-07-25 | 0:20 | 0:13 | 0:20 | 0:15
| 2019-07-26 | 0:44 | 0:35 | 0:41 | 0:36
| 2019-07-29 | 0:29 | 0:19 | 0:27 | 0:18
| 2019-07-31 | 3:51 | 2:52 | 2:06 | 2:00
| 2019-08-01 | 2:31 | 2:11 | 2:05 | 1:59
| 2019-08-02 | 2:10 | 1:49 | 2:04 | 1:49
| 2019-08-04 | 0:25 | 0:14 | 0:25 | 0:16
| 2019-08-05 | 3:29 | 2:53 | 2:05 | 2:00
| 2019-08-06 | 3:40 | 3:16 | 2:02 | 1:59
| 2019-08-07 | 2:48 | 2:23 | 2:00 | 1:59
| 2019-08-08 | 1:59 | 1:44 | 1:53 | 1:45
| 2019-08-09 | 0:45 | 0:34 | 0:44 | 0:33
| 2019-08-12 | 2:01 | 1:46 | 1:59 | 1:46
| 2019-08-13 | 2:07 | 1:54 | 2:03 | 1:53
| 2019-08-14 | 1:52 | 1:39 | 1:48 | 1:38
| 2019-08-15 | 2:23 | 2:08 | 2:04 | 1:59
| 2019-08-16 | 3:37 | 2:51 | 2:04 | 2:01
| 2019-08-19 | 2:19 | 2:07 | 2:05 | 2:01
| 2019-08-20 | 3:04 | 2:26 | 2:04 | 2:01
| 2019-08-21 | 0:51 | 0:43 | 0:50 | 0:44
| 2019-08-22 | 0:41 | 0:35 | 0:40 | 0:36
| 2019-08-23 | 0:32 | 0:18 | 0:28 | 0:17
| 2019-08-26 | 0:16 | 0:02 | 0:14 | 0:04
| 2019-08-27 | 1:12 | 0:56 | 1:11 | 0:57
| 2019-08-28 | 1:08 | 0:59 | 1:06 | 0:59
| 2019-08-29 | 0:19 | 0:03 | 0:19 | 0:04
| 2019-08-30 | 0:21 | 0:07 | 0:18 | 0:05
| 2019-09-04 | 0:35 | 0:20 | 0:35 | 0:17
| 2019-09-06 | 0:19 | 0:04 | 0:18 | 0:04
| 2019-09-09 | 2:04 | 1:52 | 2:04 | 1:53
| 2019-09-10 | 2:21 | 2:05 | 2:03 | 1:59
| 2019-09-11 | 2:01 | 1:45 | 1:58 | 1:44
| 2019-09-12 | 1:08 | 0:53 | 1:02 | 0:54
| 2019-09-18 | 0:16 | 0:01 | 0:16 | 0:01
| 2019-09-19 | 0:30 | 0:16 | 0:29 | 0:13
| 2019-09-25 | 0:05 | 0:01 | 0:00 | 0:00
| 2019-09-26 | 1:04 | 0:43 | 1:02 | 0:41
| 2019-10-03 | 0:34 | 0:15 | 0:33 | 0:15
| 2019-10-29 | 0:14 | 0:01 | 0:14 | 0:02
| 2019-11-19 | 0:04 | 0:01 | 0:00 | 0:00
| 2019-11-28 | 0:23 | 0:04 | 0:23 | 0:04
| 2019-12-04 | 0:10 | 0:04 | 0:09 | 0:04
| 2019-12-07 | 0:09 | 0:02 | 0:08 | 0:01
| 2019-12-17 | 0:07 | 0:05 | 0:06 | 0:05
| 2019-12-20 | 0:09 | 0:02 | 0:08 | 0:01
| 2020-01-03 | 0:26 | 0:14 | 0:22 | 0:14
| 2020-01-20 | 0:06 | 0:01 | 0:05 | 0:02
| 2020-02-17 | 0:33 | 0:29 | 0:29 | 0:27
| 2020-02-18 | 0:11 | 0:01 | 0:11 | 0:01
| 2020-02-26 | 0:08 | 0:01 | 0:07 | 0:01
| 2020-03-11 | 0:09 | 0:01 | 0:08 | 0:01
| 2020-03-12 | 0:11 | 0:03 | 0:10 | 0:02
| 2020-03-18 | 0:03 | 0:00 | 0:01 | 0:00
| 2020-03-28 | 0:05 | 0:00 | 0:00 | 0:00
| 2020-04-09 | 0:05 | 0:03 | 0:05 | 0:03
| 2020-04-14 | 1:24 | 1:16 | 1:25 | 1:15
| 2020-04-23 | 0:07 | 0:05 | 0:06 | 0:05
| 2020-05-21 | 0:25 | 0:07 | 0:25 | 0:08
| 2020-05-26 | 0:24 | 0:09 | 0:22 | 0:08
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '560MW' Peak period on/off trigger: '575MW / 555MW' Control period on/off trigger: '580MW / 560MW' from 26 May 2020
Comment: 'Opening limits and triggers set to reflect lower post-COVID impact loads - we adjust these to meet water heating service level targets, annual pricing period duration targets, and to focus load management on the periods of highest loading'
| 2020-05-27 | 1:22 | 1:14 | 1:21 | 1:15
| 2020-05-28 | 0:32 | 0:25 | 0:30 | 0:23
Comment: 'Pricing period triggers adjusted to better focus on highest loads'
Limit: '560MW' Peak period on/off trigger: '580MW / 560MW' Control period on/off trigger: '585MW / 565MW' from 29 May 2020
| 2020-05-29 | 0:14 | 0:01 | 0:14 | 0:02
| 2020-06-04 | 0:55 | 0:35 | 0:55 | 0:35
| 2020-06-05 | 1:10 | 1:00 | 1:10 | 0:59
| 2020-06-06 | 1:18 | 1:07 | 1:13 | 1:06
| 2020-06-07 | 1:01 | 0:53 | 1:00 | 0:53
Comment: 'Limit and pricing period triggers raised to match demand level observed with full load management measures in place and focus on highest loads'
Limit: '580MW' Peak period on/off trigger: '600MW / 580MW' Control period on/off trigger: '605MW / 585MW' from 8 June 2020
| 2020-06-08 | 4:12 | 3:38 | 2:07 | 2:01
| 2020-06-09 | 2:44 | 2:28 | 2:03 | 2:00
| 2020-06-10 | 1:09 | 0:55 | 1:05 | 0:55
| 2020-06-11 | 1:55 | 1:41 | 1:51 | 1:43
| 2020-06-14 | 0:19 | 0:02 | 0:16 | 0:02
| 2020-06-15 | 0:25 | 0:13 | 0:24 | 0:14
| 2020-06-18 | 1:13 | 0:57 | 1:12 | 0:59
| 2020-06-19 | 2:25 | 2:10 | 2:05 | 2:00
| 2020-06-22 | 0:52 | 0:38 | 0:52 | 0:36
| 2020-06-23 | 0:47 | 0:37 | 0:45 | 0:37
| 2020-06-24 | 1:29 | 1:02 | 1:22 | 1:01
| 2020-06-25 | 1:07 | 0:55 | 1:05 | 0:54
| 2020-06-29 | 1:24 | 1:13 | 1:25 | 1:14
| 2020-06-30 | 1:16 | 0:59 | 1:11 | 0:58
Comment: 'Limit and pricing period triggers raised temporarily to match demand level and mitigate the extent to which service levels are exceeded'
Comment: 'Temporary limit and pricing period triggers removed'
Limit: '580MW' Peak period on/off trigger: '600MW / 580MW' Control period on/off trigger: '605MW / 585MW'
Limit: '600MW' Peak period on/off trigger: '620MW / 600MW' Control period on/off trigger: '625MW / 605MW'
Limit: '620MW' Peak period on/off trigger: '630MW / 610MW' Control period on/off trigger: '635MW / 615MW'
| 2020-07-01 | 4:25 | 3:56 | 2:04 | 2:01
| 2020-07-02 | 3:01 | 2:28 | 2:05 | 2:00
| 2020-07-03 | 4:03 | 3:27 | 2:04 | 2:00
| 2020-07-07 | 0:45 | 0:34 | 0:43 | 0:33
| 2020-07-08 | 1:30 | 1:10 | 1:27 | 1:10
| 2020-07-09 | 3:53 | 3:02 | 2:04 | 2:00
| 2020-07-10 | 1:41 | 1:12 | 1:26 | 1:12
| 2020-07-13 | 0:40 | 0:23 | 0:35 | 0:23
| 2020-07-14 | 3:19 | 2:49 | 2:05 | 2:00
| 2020-07-15 | 3:33 | 2:50 | 2:04 | 1:59
Comment: 'Limit and pricing period triggers raised to match demand level observed with full load management measures in place and focus on highest loads'
Limit: '590MW' Peak period on/off trigger: '610MW / 590MW' Control period on/off trigger: '615MW / 595MW' from 16 July 2020
| 2020-07-16 | 4:19 | 4:05 | 2:09 | 2:01
| 2020-07-17 | 1:23 | 1:07 | 1:20 | 1:07
| 2020-07-23 | 2:08 | 1:52 | 1:58 | 1:50
| 2020-07-24 | 3:44 | 3:02 | 2:05 | 2:01
| 2020-07-27 | 1:28 | 1:23 | 1:29 | 1:23
| 2020-07-28 | 1:51 | 1:29 | 1:49 | 1:28
| 2020-07-29 | 0:44 | 0:26 | 0:40 | 0:26
| 2020-08-10 | 0:44 | 0:26 | 0:40 | 0:23
| 2020-08-11 | 0:32 | 0:23 | 0:31 | 0:24
| 2020-08-12 | 0:21 | 0:08 | 0:21 | 0:12
| 2020-08-13 | 0:15 | 0:02 | 0:15 | 0:01
| 2020-08-17 | 1:51 | 1:32 | 1:51 | 1:34
| 2020-08-18 | 0:22 | 0:02 | 0:14 | 0:03
| 2020-08-25 | 0:25 | 0:11 | 0:25 | 0:11
| 2020-08-26 | 0:43 | 0:35 | 0:41 | 0:36
| 2020-09-01 | 1:08 | 0:55 | 1:04 | 0:56
| 2020-09-02 | 0:20 | 0:10 | 0:18 | 0:11
| 2020-09-03 | 2:19 | 1:58 | 2:06 | 1:55
| 2020-09-21 | 0:11 | 0:02 | 0:11 | 0:03
| 2020-09-30 | 1:02 | 0:47 | 0:59 | 0:49
| 2021-01-12 | 0:06 | 0:01 | 0:05 | 0:01
| 2021-01-27 | 4:25 | 3:16 | 2:03 | 2:00
| 2021-03-01 | 0:09 | 0:01 | 0:08 | 0:01
| 2021-03-24 | 0:12 | 0:10 | 0:11 | 0:08
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Limit: '590MW' Peak period on/off trigger: '610MW / 590MW' Control period on/off trigger: '615MW / 595MW' from 13 May 2021
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2021-05-13 | 0:39 | 0:28 | 0:39 | 0:30
| 2021-05-17 | 0:06 | 0:01 | 0:05 | 0:01
| 2021-05-24 | 0:50 | 0:29 | 0:49 | 0:32
| 2021-05-25 | 0:49 | 0:28 | 0:40 | 0:28
| 2021-05-26 | 1:24 | 1:11 | 1:17 | 1:13
| 2021-05-31 | 0:54 | 0:41 | 0:50 | 0:42
| 2021-06-01 | 0:23 | 0:12 | 0:19 | 0:10
| 2021-06-02 | 1:12 | 0:57 | 1:08 | 0:59
| 2021-06-03 | 1:27 | 1:02 | 1:18 | 1:01
| 2021-06-04 | 0:35 | 0:25 | 0:34 | 0:26
| 2021-06-12 | 0:56 | 0:01 | 0:46 | 0:02
| 2021-06-15 | 0:28 | 0:01 | 0:28 | 0:02
| 2021-06-17 | 0:50 | 0:37 | 0:45 | 0:37
| 2021-06-18 | 0:28 | 0:15 | 0:20 | 0:11
| 2021-06-21 | 0:29 | 0:10 | 0:25 | 0:11
| 2021-06-22 | 1:26 | 1:07 | 1:25 | 1:12
| 2021-06-23 | 1:07 | 0:51 | 1:07 | 0:52
| 2021-06-24 | 1:37 | 1:17 | 1:35 | 1:17
| 2021-06-28 | 1:34 | 1:16 | 1:33 | 1:22
Comment: 'Limit and pricing period triggers temporarily increased 20MW to mitigate the extent to which service levels are exceeded in response to very cold weather'
Limit: '610MW' Peak period on/off trigger: '630MW / 620MW' Control period on/off trigger: '635MW / 615MW'
| 2021-06-29 | 5:24 | 4:34 | 2:16 | 2:11
| 2021-06-30 | 1:18 | 1:04 | 1:14 | 1:05
| 2021-07-01 | 1:14 | 0:56 | 1:09 | 0:56
| 2021-07-02 | 1:13 | 0:58 | 1:12 | 0:57
| 2021-07-04 | 0:30 | 0:13 | 0:30 | 0:16
| 2021-07-05 | 1:04 | 0:47 | 1:01 | 0:46
| 2021-07-07 | 0:58 | 0:35 | 0:53 | 0:37
| 2021-07-08 | 2:43 | 2:23 | 2:02 | 1:59
| 2021-07-09 | 3:04 | 2:45 | 2:04 | 1:59
Comment: 'Limit and pricing period triggers temporarily increased 20MW to mitigate the extent to which service levels are exceeded in response to cold weather'
Limit: '610MW' Peak period on/off trigger: '630MW / 620MW' Control period on/off trigger: '635MW / 615MW'
| 2021-07-12 | 4:25 | 4:04 | 2:03 | 1:59
| 2021-07-13 | 3:37 | 3:20 | 2:05 | 2:00
Comment: 'Limit and pricing period triggers permanently increased 10MW recognising underlying load growth shown by extent of shedding and controlled peaks exceeding the limit'
Limit: '600MW' Peak period on/off trigger: '620MW / 600MW' Control period on/off trigger: '625MW / 605MW'
| 2021-07-14 | 4:04 | 3:41 | 2:10 | 2:01
| 2021-07-15 | 0:09 | 0:01 | 0:09 | 0:01
| 2021-07-19 | 0:13 | 0:01 | 0:00 | 0:00
| 2021-07-20 | 1:09 | 0:52 | 1:09 | 0:53
| 2021-07-22 | 0:54 | 0:34 | 0:49 | 0:35
| 2021-07-23 | 0:30 | 0:16 | 0:25 | 0:19
| 2021-07-28 | 0:58 | 0:44 | 0:59 | 0:44
| 2021-07-29 | 1:08 | 0:52 | 1:06 | 0:53
| 2021-08-03 | 2:11 | 1:37 | 1:56 | 1:35
| 2021-08-04 | 1:10 | 0:56 | 1:07 | 0:57
| 2021-08-08 | 1:31 | 1:06 | 1:30 | 1:10
| 2021-08-09 | 5:14 | 4:34 | 2:39 | 2:34
Comment: 'Limit and pricing period triggers temporarily increased 40MW to mitigate the extent to which service levels are exceeded in response to very cold weather'
Limit: '640MW' Peak period on/off trigger: '660MW / 640MW' Control period on/off trigger: '665MW / 645MW'
Comment: 'Limit and pricing period triggers temporarily increased 20MW to mitigate the extent to which service levels are exceeded in response to very cold weather'
Limit: '660MW' Peak period on/off trigger: '680MW / 660MW' Control period on/off trigger: '685MW / 665MW'
Comment: 'Limit and pricing period triggers temporarily increased 20MW to mitigate the extent to which service levels are exceeded in response to very cold weather'
Limit: '680MW' Peak period on/off trigger: '700MW / 680MW' Control period on/off trigger: '705MW / 685MW'
Comment: 'Temporary limit and pricing period triggers removed'
Limit: '600MW' Peak period on/off trigger: '620MW / 600MW' Control period on/off trigger: '625MW / 605MW'
| 2021-08-10 | 1:50 | 1:35 | 1:51 | 1:37
| 2021-08-11 | 0:35 | 0:25 | 0:34 | 0:26
Comment: 'Limit and pricing period triggers permanently increased 15MW recognising underlying load growth shown by extent of shedding and controlled peaks exceeding the limit'
Limit: '615MW' Peak period on/off trigger: '635MW / 615MW' Control period on/off trigger: '640MW / 620MW'
| 2021-08-16 | 0:20 | 0:07 | 0:15 | 0:09
| 2021-08-30 | 0:22 | 0:01 | 0:00 | 0:00
| 2021-09-15 | 0:38 | 0:25 | 0:36 | 0:23
| 2021-09-16 | 0:48 | 0:24 | 0:44 | 0:26
| 2021-09-28 | 0:19 | 0:07 | 0:16 | 0:05
| 2021-10-12 | 4:08 | 3:46 | 2:44 | 2:36
| 2021-10-13 | 1:55 | 1:37 | 1:50 | 1:35
| 2021-10-14 | 0:20 | 0:06 | 0:20 | 0:05
| 2021-10-21 | 0:06 | 0:01 | 0:05 | 0:01
| 2021-11-09 | 2:30 | 0:05 | 0:00 | 0:00
| 2022-01-02 | 0:19 | 0:04 | 0:14 | 0:01
| 2022-01-10 | 0:23 | 0:13 | 0:22 | 0:16
Agreed service level target: 'Business: Maximum of 2 hours off in any 5 hour period'
Agreed service level target: 'Residential: Maximum of 4 hours off in any 8 hour period'
Limit: '615MW' Peak period on/off trigger: '635MW / 615MW' Control period on/off trigger: '640MW / 620MW' from 1 May 2022
Comment: 'Opening limits and triggers set to last year's closing levels - we change these to the extent required to meet customer demand - changes aim to focus load management on the periods of highest loading, meet service level targets and achieve the target annual duration for pricing periods'
| 2022-05-10 | 0:30 | 0:18 | 0:29 | 0:19
| 2022-05-12 | 1:15 | 0:53 | 1:14 | 0:57
| 2022-05-13 | 0:21 | 0:05 | 0:20 | 0:07
| 2022-05-23 | 0:20 | 0:06 | 0:15 | 0:06
| 2022-05-24 | 1:02 | 0:52 | 1:01 | 0:51
| 2022-05-25 | 0:53 | 0:43 | 0:49 | 0:44
| 2022-05-26 | 0:29 | 0:13 | 0:25 | 0:12
| 2022-05-27 | 1:30 | 1:14 | 1:27 | 1:16
| 2022-06-13 | 0:51 | 0:38 | 0:49 | 0:40
| 2022-06-14 | 0:49 | 0:37 | 0:41 | 0:36
| 2022-06-15 | 1:32 | 1:20 | 1:27 | 1:22
| 2022-06-20 | 1:09 | 0:53 | 1:00 | 0:53
| 2022-06-21 | 1:13 | 0:59 | 1:11 | 1:01
| 2022-06-22 | 4:03 | 3:37 | 2:04 | 1:59
| 2022-06-23 | 4:06 | 3:46 | 2:30 | 2:24
| 2022-06-27 | 0:29 | 0:14 | 0:24 | 0:13
| 2022-06-28 | 0:58 | 0:40 | 0:55 | 0:41
| 2022-06-29 | 2:08 | 1:53 | 2:01 | 1:54
| 2022-06-30 | 3:24 | 2:56 | 2:03 | 2:00
| 2022-07-01 | 2:19 | 1:58 | 2:04 | 1:56
| 2022-07-04 | 1:01 | 0:49 | 0:56 | 0:47
| 2022-07-05 | 1:11 | 0:58 | 1:10 | 0:59
| 2022-07-06 | 1:01 | 0:49 | 0:51 | 0:47
| 2022-07-07 | 2:28 | 2:13 | 2:02 | 2:00
| 2022-07-11 | 4:38 | 4:13 | 2:07 | 2:01
| 2022-07-12 | 4:36 | 3:41 | 2:03 | 1:59
| 2022-07-17 | 0:20 | 0:04 | 0:13 | 0:01
| 2022-07-20 | 0:40 | 0:21 | 0:40 | 0:20
| 2022-07-21 | 2:02 | 1:50 | 1:57 | 1:49
| 2022-07-22 | 1:28 | 1:16 | 1:25 | 1:16
| 2022-07-25 | 1:43 | 1:23 | 1:39 | 1:23
| 2022-07-26 | 0:47 | 0:34 | 0:44 | 0:34
| 2022-07-28 | 0:20 | 0:08 | 0:19 | 0:08
| 2022-07-29 | 0:26 | 0:10 | 0:26 | 0:10
| 2022-08-01 | 2:49 | 2:27 | 2:04 | 1:59
| 2022-08-08 | 1:50 | 1:31 | 1:47 | 1:31
| 2022-08-09 | 2:19 | 2:06 | 2:04 | 1:59
| 2022-08-10 | 3:41 | 3:08 | 2:08 | 2:01
| 2022-08-11 | 1:58 | 1:45 | 1:55 | 1:45
| 2022-08-12 | 3:32 | 3:03 | 2:04 | 1:55
| 2022-08-15 | 3:09 | 2:44 | 2:04 | 1:59
| 2022-08-16 | 0:18 | 0:01 | 0:17 | 0:01
| 2022-08-29 | 0:00 | 0:00 | 0:03 | 0:00
| 2022-08-30 | 0:29 | 0:17 | 0:24 | 0:17
| 2022-08-31 | 0:27 | 0:11 | 0:21 | 0:07
| 2022-09-05 | 2:14 | 2:04 | 2:05 | 2:00
| 2022-09-06 | 3:29 | 3:01 | 2:02 | 1:59
| 2022-09-07 | 2:45 | 2:27 | 2:04 | 2:00
| 2022-09-08 | 0:08 | 0:01 | 0:00 | 0:00
| 2022-09-14 | 0:45 | 0:36 | 0:44 | 0:37
| 2022-09-15 | 1:27 | 1:16 | 1:23 | 1:15
| 2022-10-05 | 2:29 | 2:13 | 2:05 | 2:00
| 2022-10-06 | 4:35 | 3:55 | 2:08 | 2:01
| 2022-10-07 | 1:34 | 1:13 | 1:20 | 1:08
| 2022-10-12 | 0:03 | 0:00 | 0:02 | 0:00
| 2022-10-14 | 0:19 | 0:01 | 0:06 | 0:01
| 2022-10-18 | 0:30 | 0:16 | 0:25 | 0:16
| 2022-10-19 | 0:45 | 0:32 | 0:44 | 0:34
| 2022-10-20 | 0:20 | 0:08 | 0:17 | 0:07
| 2022-10-25 | 0:24 | 0:08 | 0:17 | 0:08
| 2023-03-28 | 2:54 | 0:56 | 2:03 | 0:57
| 2023-03-29 | 0:45 | 0:01 | 0:39 | 0:02
| 2023-03-30 | 4:19 | 1:26 | 2:03 | 0:54
| 2023-04-11 | 0:02 | 0:00 | 0:00 | 0:00
| 2023-04-12 | 3:04 | 3:00 | 2:06 | 2:01
| 2023-04-13 | 3:11 | 2:59 | 2:04 | 2:00
| 2023-04-15 | 3:08 | 3:00 | 2:04 | 2:00
| 2023-04-16 | 3:34 | 3:06 | 2:03 | 1:59
| 2023-04-17 | 3:18 | 3:10 | 2:04 | 2:00
| 2023-04-18 | 3:32 | 3:14 | 2:04 | 2:00
| 2023-04-19 | 3:03 | 2:57 | 2:04 | 2:00
| 2023-04-22 | 3:24 | 2:56 | 0:00 | 0:00
| 2023-04-23 | 0:11 | 0:00 | 0:00 | 0:00
| 2023-04-26 | 0:00 | 0:00 | 2:04 | 2:01
| 2023-04-27 | 0:00 | 0:00 | 2:04 | 2:01
| 2023-04-30 | 3:14 | 3:01 | 0:00 | 0:00
| 2023-05-11 | 2:54 | 2:20 | 2:04 | 2:00
| 2023-05-16 | 1:22 | 1:08 | 1:22 | 1:08
| 2023-05-17 | 1:02 | 0:48 | 1:02 | 0:50
| 2023-05-23 | 0:30 | 0:14 | 0:30 | 0:14
| 2023-05-25 | 0:38 | 0:25 | 0:35 | 0:25
| 2023-05-29 | 3:24 | 0:26 | 0:00 | 0:00
| 2023-05-31 | 0:12 | 0:05 | 0:10 | 0:06
| 2023-06-01 | 2:58 | 0:44 | 0:00 | 0:00
| 2023-06-06 | 3:01 | 0:35 | 0:56 | 0:40
| 2023-06-07 | 3:23 | 3:00 | 2:06 | 2:01
| 2023-06-08 | 1:38 | 1:24 | 1:36 | 1:27
| 2023-06-09 | 1:25 | 1:05 | 1:23 | 1:08
| 2023-06-12 | 1:10 | 0:55 | 1:08 | 0:59
| 2023-06-13 | 1:06 | 0:52 | 1:04 | 0:52
| 2023-06-14 | 1:00 | 0:47 | 1:01 | 0:50
| 2023-06-15 | 0:27 | 0:16 | 0:25 | 0:18
| 2023-06-16 | 0:23 | 0:01 | 0:00 | 0:00
| 2023-06-19 | 3:03 | 0:23 | 0:00 | 0:00
| 2023-06-20 | 3:04 | 0:24 | 0:00 | 0:00
| 2023-06-21 | 3:01 | 0:35 | 0:00 | 0:00
| 2023-06-22 | 3:01 | 0:37 | 0:00 | 0:00
| 2023-10-19 | 2:17 | 2:05 | 2:17 | 2:01
| 2023-11-02 | 8:00 | 0:05 | 0:19 | 0:07
| 2023-11-03 | 8:00 | 0:04 | 0:00 | 0:00
| 2023-11-09 | 0:50 | 0:35 | 0:51 | 0:35
| 2023-11-22 | 0:25 | 0:18 | 0:24 | 0:19
| 2023-11-23 | 1:07 | 1:01 | 1:07 | 1:02
| 2023-11-24 | 8:00 | 0:08 | 0:00 | 0:00
| 2023-11-27 | 0:37 | 0:31 | 0:36 | 0:32
| 2023-12-04 | 2:01 | 1:47 | 1:58 | 1:47
| 2023-12-07 | 1:33 | 0:57 | 1:23 | 1:00